# INSPECTION FINDINGS

In compliance with the instructions of (Client Name), SGS inspection team carried out visual examination, witnessing of functional test and load test exercise at their site (Site Location).

| Name of Client | : |  |
| --- | --- | --- |
| Identification | : |  |
| SGS Order No. |  |  |
| Make | : |  |
| Model | : |  |
| Manufacturer Serial Number | : |  |
| Capacity | : |  |
| Location | : |  |
| Inspection Date | : |  |
| Status | : | Satisfactory or Unsatisfactory |
| Type | : |  |
| Levels | : |  |
| Reference Code For Inspection | : | ASME A-17.1 / A-17.2 / EN-81 (Safety Code For Elevators and Escalators) |

Following points were checked during the inspection activity to ensure safe operational condition along with proper working of safety devices.

## ITEM

### ALARM BELL & EMERGENCY TELEPHONE

| Check Points | Remarks/Recommendations |
| --- | --- |
| - Alarm operation |  |
| - Response System |  |

### SAFETY EDGE, SENSORS & CAR

| Check Points | Remarks/Recommendations |
| --- | --- |
| - Condition and operation of the safety edges and door sensors. |  |
| - Check the door closing pressure is appropriate for the particular environment. |  |
| - Maximum allowable Load capacity found marked at each floor. |  |
| - Check for floor levelling in both the "up" and "down" direction. |  |
| - Check for damage of push buttons, missing covers and sharp protruding edges. |  |
| - Check for operation of cabin operating panel and LOP (Landing Operating Panel). |  |
| - Check the condition and operation of fire safety switch. |  |
| - Check the condition and operation of seismic device. |  |
| - Check the condition and operation of overload protection device. |  |

### CAR DOORS/GATES

| Check Points | Remarks/Recommendations |
| --- | --- |
| - Check adjustment and wear. Gaps between sliding doors and architrave. |  |
| - Check for wear in door sill tracks and door shoes which can also give rise to this condition. |  |
| - Check for potential gap between multi leaf doors at bottom when closed. (Door hanger rollers/eccentric rollers). This check may be more conveniently carried out from inside the lift well enclosure. |  |
| - The vision panel in solid doors must be the wired glass type. |  |

- MOTOR & PULLEY ROOMS

| Check Points | Remarks/Recommendations |
| --- | --- |
| - Check door is locked and prescribed hazard warning notice fitted. |  |
| - Check motor room door key is held by a responsible person on site or a notice as to the whereabouts provided |  |
| - Check motor room access route is safe and free from obstructions. |  |
| - Check proper ventilation system or air condition unit for maintain ambient temperature. |  |
| - Check availability of fire protection device (fire extinguisher) and lighting system. |  |
| - Check it is adequately lit and clean and tidy. |  |
| - Sitting of equipment: Check components such as controller, traction unit, governor and selector (if fitted) are sited so as to provide safe access for maintenance and inspections. |  |
| - Guarding/hazard markings. Where a hazard may result, appropriate guarding and/or hazard markings may be required |  |
| - Check all prescribed notices are prominently displayed (Hand winding instructions and Electric Shock treatment). |  |
| - Check the maintenance log book is in order, properly compiled and up to date. |  |

.

- CONTROL PANELS & ELECTRICAL EQUIPMENT

| Check Points | Remarks/Recommendations |
| --- | --- |
| - Check all electrical equipment is suitably housed. |  |
| - Check main isolation switch is readily accessible adjacent to motor room/compartment door. |  |
| - Check inside controller doors, attention being paid to condition of wiring and components, presence of electric arc splash guards and labelling of overload circuit breakers, settings and fuse ratings. |  |
| - Check no flammable papers or materials are stored inside or on top of the controller. (Remove immediately any hot papers etc.). |  |
| - Check for operation of ARD (Automatic Rescue Device) |  |

- TRACTION UNIT

| Check Points | Remarks/Recommendations |
| --- | --- |
| - Check all accessible components for condition, attention being given to security of split pins and grub screws retaining brake parts, brake shoes and drums. |  |
| - The gear oil level indicator should be checked. |  |
| - Check the condition of the suspension rope, remembering that with the car at top level, the sections of rope over the traction sheave will not be accessible when inspecting the be rope from the car top. |  |
| - Check the condition and traction pulley and cabin / counter weight pulley |  |
| - Check that emergency release is either fitted or available. |  |

- CAR TOP & WELL ENCLOSURE

| Check Points | Remarks/Recommendations |
| --- | --- |
| - Using the site emergency lift door release key, access the top of the lift car at top floor level. Operate the emergency stop button without delay. |  |
| - Check that the car top is safe and satisfactory, paying attention to lose wiring or other loose material, which may cause a trip hazard. Spilt oil from a leaking gear unit above may cause slippery surfaces. There may be an excessive unguarded gap between the car top perimeter and the well wall. |  |
| - Check by hand the operation of the maintenance limit first, if possible, remembering that if the car is driven up onto some types of "ultimate limit", resetting from the controller may be required. |  |
| - Check limit stops car 1.8m below well ceiling or nearest obstruction. |  |
| - Check for presence of "restricted headroom" notices where appropriate. |  |
| - Check an "up" ultimate limit is provided. |  |
| - Check the lift well enclosure is complete and has no loose panels. |  |
| - Check "other services" which may be run in the corner of the well enclosure – Check they are safe and adequately fixed. |  |
| - Check tightness of fixing bolts on car and balance weight guide brackets. |  |
| - Check car guides alignment. |  |
| - Check condition of suspension belts over entire length (if possible) including termination. |  |
| - Check condition of balance weight and attachments to ensure that there is no contact between weights and well wall during travel. |  |
| - Check tie rod lock nuts and split pins are secure. |  |
| - Check suspension rope, compensatory belt and idle rope (if fitted) terminations. |  |
| - Check trailing flexes for abrasion caused by well wall or pit floor contact and damage caused by snagging. |  |
| - Drive car down onto the bottom maintenance control stopping limit using the car top controls. |  |
| - Check that when car stops it does not contact pit buffers. |  |

- LANDING DOORS

| Check Points | Remarks/Recommendations |
| --- | --- |
| - Check locks securely fixed and lock covers fitted. |  |
| - Check that power operated doors incorporate pre-locking feature. |  |
| - Check emergency lock release mechanism is working. |  |
| - Check landing door emergency release escutcheon plates are satisfactory. |  |
| - Check on multi leaf systems that mechanical linkage is provided or slave contacts fitted. |  |
| - Check steel wire and nylon door closer cords for broken wires/cut fibres and verify terminations are satisfactory. |  |
| - Check condition of door stops/buffers. |  |
| - Check correct adjustment on headers and eccentric rollers (forced gap at bottom of doors is less than 10mm). Check that the locknuts on rollers and adjusters are tight. |  |
| - Check top and bottom tracks, door frames are securely fixed to steelwork or brickwork. |  |
| - Check presence and condition of toe guards appropriate to door opening operation. |  |
| - Check landing and car door shoes are adequately and securely fixed. Check for corrosion of mild steel shoe brackets where serious corrosion and damage can result from action of fluids in sill tracks (cleaning fluids), coupled with abuse and vandalism. |  |
| - The vision panels in solid landing doors should be the wired glass. | Not applicable |

- LIFT WELL PIT

| Check Points | Remarks/Recommendations |
| --- | --- |
| - Access the lift well pit from the bottom landing using the emergency door release key. |  |
| - Ensure that there is safe means of access and that the pit is in all other respects safe and satisfactory. The presence of paper and/or other flammable rubbish should be reported for urgent removal. |  |
| - Check that the pit is of sufficient depth to provide survival space for a person, under car in a compressed buffer condition. |  |
| - Check that a pit stop switch is fitted and in the correct position. |  |
| - Check the condition of all pit mounted equipment making note of any damage caused by ingress of water or flooding. |  |
| - Check balance weight guard fixings. |  |
| - Check the car/balance weight buffers are securely fixed and correctly positioned. |  |
| - Check adjustment of broken rope/idle rope weight switches – would weight meet any obstruction before switch operates. |  |
| - Send Car to top floor landing and check the balance weight run by clearance is satisfactory. |  |
| - Check all attachments underneath lift car. |  |
| - Check the safety gear type is appropriate for the type of lift. |  |
| - Check free movement of safety gear linkages by hand, if possible. |  |
| - Check the underside of lift car is provided with an adequate car apron. |  |

- LOAD TEST EXERCISE

| Description | Result |
| --- | --- |
| 10.1 Rated Capacity Load Test - Load the elevator with 100% of its rated capacity using calibrated test weights. - Run the lift from bottom floor to top floor and then back down. - Ensure the elevator stops at every floor during operation. - Check brake performance & leveling accuracy. Check for abnormal noise and excessive vibration | Empty |
| 10.2 Proof Load Test (110%) - Load the elevator with 110% of its rated capacity using calibrated test weights. - Run the lift from bottom floor to top floor and then back down. - Ensure the elevator stops at every floor during operation. - Check brake performance & leveling accuracy. - Check for abnormal noise and excessive vibration | Empty |
| 10.3 Brake Performance Test - Load the elevator with 125% of its rated capacity. - Keep the load applied for 8 to 10 minutes. - Ensure the elevator does not move during this time. - Verify that the elevator does not slip or change its level (no upward or downward movement). | Empty |

# MAJOR FINDINGS:

# MINOR FINDINGS (AREA OF IMPROVEMENT):

| Next Examination Due on | : | (If report is satisfactory the next inspection date after six month or for unsatisfactory report next inspection date not applicable) |
| --- | --- | --- |
| Conclusion | : | Satisfactory: On the behalf of visual, operation examination and load test exercise the subject elevator was found satisfactory at the time of inspection and fit for intended use. Unsatisfactory: On the behalf of visual and operation examination the subject elevator was found unsatisfactory at the time of inspection and not fit for intended use. |

# SGS Pakistan (Private) Ltd.

Photographic Presentation

| Cabin | Machine Room |
| --- | --- |
| Pit Area | Shaft |
| Car top | Control Panel |